## Governance Reporting
Water Safety Joint Working Group Action Plan as at 16 March 2017 on Recommendations from the Inquiry Panel
|  | RECOMMENDATIONS | ACTION | RESPONSIBILITY | TIMELINE | RISKS / COMMENT / UPDATE | STATUS: Red (off-track); Amber (on-track with issues); Green (on-track)
Column3 | Column32 | Column12 | Column4 | Column5 | Column6 | Column7 | Column8
a) |  | The joint working group (Water Safety JWG), which has been set up with representatives from HDC, HBRC, DHB and the Drinking-Water Assessors (DWA), continue its work with each of its members committing to co-operate with each other and work positively in the interests of drinking-water safety. | Status, ongoing utility/value of group to be reviewed within 12 months. Terms of Reference and 'Ground Rules' for JWG agreed NCC representatives fully engaged. Chair discussing future scope, structure and resourcing of JWG with Mayors and CEOs. Draft Terms of reference developed for HB Water Governance Joint Committee (currently with CEOs for review) - ToR to be confirmed and Governance group established. HBRC agreed to provide additional support to JWG, with project management and secretariat - Details to be confirmed | Chair | 2017-04-01
b) |  | The Water Safety JWG meet regularly, and as frequently as required, to maintain effective oversight of all issues relating to the safety of the Havelock North drinking-water supply for at least the 12 months from 12 December 2016. | Agreed 3rd Thursday of each month as follows: Jan 19th, Feb 16th, March 16th, April 20th, May 18th, June 15th, July 20th, Aug 24th (4th Thurs as in China on 3rd), Sep 21st, Oct 19th, Nov 16th Timings confirmed 3.00pm to 5.00pm Chair to call additional meetings as required | Chair |  |  | Completed
c) |  | The Water Safety JWG members notify each other, and keep each other informed, of any information that could affect drinking-water-safety risks | Members to individually consider WHAT information should be shared - as both a sender and receiver of information Members also to consider what are seem as 'Drinking Water Safety Risks' Above issues to be discussed at a Workshop to be hosted by HBRC and a consensus paper developed to reflect common understanding and requirements for information sharing Framework on HOW such information will be shared will then be developed and distributed Once agreed by JWG, paper to be shared with Mayors/CEOs and resourcing issues addressed. | Members/HBRC | 2017-04-01 | Date for half day Workshop set for 4 Apr 17 Comms strategy to be linked/updated based on outcomes of workshop.
| JWG | Transgression Notification Process | To be considered as part of above process | Members/HBRC | 2017-04-01
d) |  | The Water Safety JWG investigate aquifer matters of potential relevance to drinking-water safety over the next 12 months. | Members provided with a presentation on what is currently being done (include modelling) by HBRC - NCC representatives to be updated Issues/gaps that still need to be addressed - Agencies to identify additional measurement options, gaps and issues JWG to discuss/agree how these gaps/issues will be addressed and in what priority order 'White Paper' to be developed to capture/address relevant issues | HBRC HDC | 2017-04-01 | Need to ensure JWG integrates with (but not duplicates) work being undertaken by TANK Potential planning, budgeting and policy issues could come up through this process, which will need to be referred to appropriate agencies eg Drinking Water protection ZonesHBRC groundwater model presented to the group on the 19th. Copies of the presentation provided to all members. HBRC will continue to pursue with the group what application it sees for the model in assessing risks to drinking water supplies, and what scenarios need to be examined. This work will be ongoing for sometime and is intended to feed into the collaborative policy development process (TANK). Project management resource from HBRC to facilitate/develop potential structure/contents of 'White Paper'.
| JWG | Bore Security | Letter from HBRC to HDC indicating 'possibility that bores covered by resource consent WP070080Tb may not meet condition 21 of that consent in a similar way to to Brookvale bores 1,2 and 3'. HDC seeking to develop a practical approach which enables HDC to undertake appropriate tests that will be recognised and accepted by DWA and HBRC without duplicating effort and cost. Group to develop criteria and process for testing, inspecting, verification and reporting. | HBRC & HDC |  | BV3 bore head was inspected by HBRC staff on 28/2/17. On the basis of the report (by Honnors Welldrilling) and the site visit HBRC are satisfied that compliance with condition 21, WP070080Tb has been demonstrated. | Completed
| JWG | Consents of Regional Significance | HBRC to prepare a memo of current practice Members to respond on additional requirements and/or what needs to change | HBRC Members | 2017-04-01 | To be included with NES Interface (below)
| JWG | NES Interface | HBRC to set out how it is working - what the current process is Members to provide feedback/comment | HBRC Members | 2017-04-01
| JWG | Secure Water Protection Zones | To be considered as part of the White Paper process under d) | HDC | 2017-04-01 | T&T Investigations commenced with Eastbourne to assess bore field, determine the extent of influence and recommend an appropriate zone for catchment risk assessments to commence.
| JWG | Reporting to TANK - DWS Position | Chair to investigate options with Mayors/CEOs on how best the 2 working groups will link/liaise/coordinate. Potentially include in a) above | Chair | 2017-04-01 | Identified mutual relationship between TANK and JWG and need for direct linkage. To be covered by proposed Water Governance Joint Committee - ToR under development
| JWG | Updating DWS Bore Locations in GIS | Municipal bores to be checked/updated - included in groundwater model Investigations to be carried out on current level of accuracy of the rest and options for getting to desired level - to include potential costs Data matching to be used where possible | HDC/NCC HBRC | 2017-04-01 | DWA advised of potential enhanced accuracy with system update in July. Still significant potential for inaccuracies. Massive job to get all in. Noted that JWG should discuss potential bore inundation risk given recent events up north.
| JWG | Water Aging | To be considered as part of the White Paper process under d) | HBRC HDC | 2017-04-01 | Acknowledged as a significant 'current' issue. Needs significant work and input from GNS. HDC and NCC now age testing some bores - some on seasonable basis. HBRC developing Heretaunga Plains report on aging
e) |  | The Water Safety JWG investigate whether the Havelock North reticulation and distribution systems are fragile or vulnerable and whether they need maintenance, repair work, or improvements, in order to deliver safe drinking water to consumers. To include 'backflow protection' - per Nathan Gedye 30/1/17 | A Framework and Guidelines to be provided that covers current asset assessments, practices and processes in place, risks and mitigation plans, effects of chlorination and hydraulic modelling, for review Waugh Infrastructure to provide JWG independent advice on adequacy/appropriateness of systems | HDC | 2017-04-01 | Available documents:HDC Asset Management Plan, independent review on AMP, Hansen Mtce reports, asset reports (age, material, date) spatial distributions, critical assets. Contractor work practices, 3rd party damage risks. Retic performance using current modelling and water quality through monitoring (DBPs, biofilm etc.).
f) |  | Following inspection and any necessary maintenance and/or repair work on the Brookvale bore 3 equipment, the Water Safety JWG should approve the condition of Brookvale bore 3 prior to its use as a drinking-water supply. | JWG met all initial requirements 'No objection' to use of BV3 received from Inquiry on 3 March 2017, subject to provision of operating manual and maintenance & inspection programme As part of the catchment survey 2 key risk areas were noted as risks from the modelling. The intention had been to Dye trace these 2areas to confirm (or otherwise the risk noted in the T&T modelling). Given potential risks HDC have asked T&T to consider what alternatives, timing etc for the investigation. Recommendation is to manage these areas AS a RISK as per the modelling outcomes. The Dye testing will occur at a later date (over winter when water demand is lower - this would allow for a scenario of a very slow 'show' without affect the drinking water and treatment plant). The RISK mitigations are being included in the WSP and need to be agreed by the JWG | HDC | 2017-06-01 | BV3 now operating - Treatment will be equivalent to treatment of surface water. Operation ceased with rain event over Xmm, provide a higher level of monitoring of discharge activities in the catchment, review of consents and activities that could trigger
g) |  | The Water Safety JWG should, prior to its use as a drinking­ water supply, approve a maintenance and inspection schedule for Brookvale bore 3 for at least the 12 months from 12 December 2016. | The new plant maintenance and inspection requirements are currently being compiled (whilst commissioning is occuring). This needs to be joined up with the other maintenance inspection items. This will start paper based whilst the inspection programmes and forms are created in the electronic manaintenance management system. Report to be circulated with DWA report as above in f) | HDC | 2017-03-01 | Work still proceeding, with the Treatment plant details feeding in. Risk to get all operational in electronic system could create delays so a manual documentation process will be in place until the electronic system is operational
h) |  | For at least the 12 months commencing 12 December 2016, log 5 level of treatment be applied to Brookvale bore 3 drinking water (being cartridge filtration, UV and chlorination), with the Water Safety JWG to: | Underway, programme for implementation available if required. Monitoring of operation will be provided as per monitoring report requirements defined in NZDWS which are extensive in regards to these treatment processes. | HDC | Ongoing | Plant commenced operation on 7/3/17. Operation and performance being monitored and supported by Controlbox, H2Ope and electrical/mechanical suppliers.
| i) | Approve the selection and commissioning of the equipment; and | Completed | HDC
| ii) | Oversee the training and operational procedures for the treatment equipment and processes | Project suppliers have handover requirements, initial discussions with other Councils underway. To be signed off as part of DWA Report JWG to be invited for site visit once plant operational | HDC | 2017-04-01 | Operations and maintenance manuals from suppliers. FD and updates once plant is operational Set up meeting with Rotorua DC operators on UV treatment/operations/maintenance. Licence to Operate training commenced. Training in instrumentation validation and calibration Thursday 16/3
i) |  | For at least the 12 months commencing 12 December 2016, the Hastings water will be treated with chlorination, and that the Water Safety JWG should keep under review the nature and extent of treatment required to ensure the safety of the Hastings water being supplied to Havelock North | Issue to be considered as part of regular monthly review of a monitoring/compliance report | HDC | Monthly | HDC have agreed. Updates will be provided as new information comes to hand. | Ongoing
j) |  | For at least the 12 months commencing as soon as practicable (but before Brookvale bore 3 is reactivated), monitoring and testing of the Havelock North and Hastings drinking-water supplies take place in accordance with the recommendations of Dr Fricker dated 6 December 2016 and, in particular, that the following minimum monitoring shall be carried out: | Issues to be considered as part of regular monthly review of a monitoring/compliance report HDC to provide draft template for monthly reporting Once commenced, monthly reports will need to be available at least two full days before each meeting | HDC | Monthly | HDC monitoring programme in accordance with specification and DWA approval. V2.1 of the plan previously provided to the inquiry is being updated currently for DWA and JWG approval | Ongoing
| i) | 2-litre raw water samples be taken daily from each bore contributing to the supply of Havelock North drinking water; | Approach agreed and testing underway and reported Need to agree on protocol for circumstances if a presence is found in the 2l investigation sample. Advice from Dr Fricker has been received - JWG to discuss and agree approach | HDC/DWA | Ongoing | External advisor being engaged to assist HDC and JWG with monitoring plan, results interpretation and water quality advice | .
| ii) | total coliform and E.coli testing, using either Colilert 18 or such other effective and speedy test that the DWA approves; | DWA to advise/agree appropriate targets Monitoring/compliance report to be produced/reviewed monthly . | DWA HDC | 2017-04-01 | Process in place with WTHB. Work underway
| iii) | enumerated tests for all reticulation samples and presence/absence testing for the 2 litre samples from the bores; | Monitoring/compliance report to be produced/reviewed monthly For operational effectiveness would like to use WTHB for all the bore samples. Currently they are awaiting IANZ approval for the colilert test on the NZDWS std, they are approved for other methods. Recommend that prior to IANZ accreditation is receieved that the 100ml test be via any approved NZDWS testing method.. | HDC | Monthly | Process in place with WTHB. Results shared daily
| iv) | testing from the reticulation sites be continued in accordance with the DWSNZ and the requirements of the DWA; | New monitoring plan submitted to DWA and copied previously to JWG - requires JWG endorsement Monitoring/compliance report to be produced/reviewed monthly . | DWA | 2017-04-01 | A revised sampling plan has been submitted for DWA approval which is approximately 250% of DWSNZ requirement, the final detail site programming is to be finalised. The current higher level of reticulation sampling will continue until the details of the 250% rate is finalised and agreed with the DWAs
| v) | daily testing of FAC levels take place at the ends, and in the dead ends that are most at risk, of the reticulation with a pH level of less than 8 and with a required FAC level of at least 0.2mg/L, or an adjusted level if the pH level is greater than 8; | Monitoring/compliance report to be produced/reviewed monthly . | HDC | Monthly | Included in the revised sampling plan. Results shared daily
| vi) | testing for disinfectant by-products take place as directed by the DWA; and | DWA to provide protocol Monitoring/compliance report to be produced/reviewed monthly . | DWA | Ongoing | Work underway subject to sign off on the locations and frequency for sampling.
| vii) | the test set out in (i) be carried out three times a day during and immediately after an abnormal wet weather event (this event, and the details of such increased testing, to be defined and prescribed by the Water Safety JWG). | Pragmatic definition of what constitutes an abnormal wet weather event agreed - 'When flow in the Mangateretere reaches a trigger point' - trigger point to be recommended by HBRC in consultation with Science Caucus | HBRC | 2017-04-01 | Science caucus currently modelling scenarios to work out a trigger point HBRC to suggest a trigger if Science Caucus unable to respond by 31 March 2017.
k) |  | For at least the four months commencing 12 December 2016, testing and monitoring for protozoa shall be carried out at each bore weekly using 1,000 litre samples, with the regime thereafter to be subject to review by the Water Safety JWG for frequency but still using 1,000 litre samples. NOTE : Four month period will run from commencement of testing date, not 12/12/16 - refer Nathan Gedye email dated 14 March 2017 | Programme underway, monitoring reports to be uploaded with other monitoring data and supplied. Massey happy with WTHB as the collection agent. | HDC | Monthly | New rig created, additional rigs being created to enable the weekly programme to be achieved. Security of rig being reviewed further, looking to see if it can be implemented 'inside' the cover to provide additional security Programme has recommenced with new equipment | .
l) |  | For the purpose of recommendation (k) above, the Eastbourne bores 2 - 5 should be treated as one bore. | Bore number 5 selected for monitoring protocol | HDC |  | Advised verbally by HDC at Dec 16 meeting - Agreed | Completed
m) |  | The Water Safety JWG satisfy itself that persons carrying out sampling and testing are properly trained and competent, that the testing methods being used are as sensitive and effective as practicable, and that the test processes are being carried out in a way that is optimal in terms of timing, efficiency, and result­ reporting. | Report provided Assurance sought by Nathan Gedye (email 14 March 2017) that recommendation being pursued | HDC |  | All sampling and testing for compliance is being undertaken by laboratories that are IANZ accredited and to approved processes. The new monitoring plan notes an independent audit sample and a requirement for annual refresher of samplers. Noted issue at previous meeting wrt to the failure of one lab to follow correct testing protocol. | Completed
n) |  | An Emergency Response Plan be drafted by HDC and approved by the Water Safety JWG and the DWA before Brookvale bore 3 supplies drinking water to the reticulation. | Plan to be produced, considered and approved | HDC | 2017-04-01 | In progress, will need to incorporate updates to WSP and any specific plans for the treatment plant. Intention is to base this on US EPA guidance document as this template provides a simple way to consolidate the key items. This will sit within Councils wider response planning framework- but be Water specific.
o) |  | If the Water Safety JWG is unable to reach unanimous agreement in relation to any matter pertaining to the safety of drinking water, advice to the Inq uiry of that should be given promptly by the Water Safety JWG Chair to counsel assisting the Inquiry. | Acknowledged | Chair | Ongoing | Nothing to report
p) |  | Brookvale bores 1and 2 should not be reactivated for drinking-water supply without at least six weeks prior notice to the Inquiry and the Water Safety JWG | HDC to remodel future reticulation options, HDC to share previous work with JWG, JWG to discuss potential supply options | HDC | Ongoing | Both bore pumps have been removed for inspection and checking of bore casings. Plan is to clean and refurbish pumps but not to reinstall unless approval is sought. HBRC was advised that BV1 is proposed to be abandoned and not used again. HDC in discussion with HBRC on potential for re-consenting Brookvale bores 2 and 3. This will help inform HDC on future water supply options and re-modelling outputs from the Optimatics study.
q) |  | NEW requirement from Inquiry 15/2/17 How do agencies view the adequacy of the testing procedures and the training, understanding and competence of all involved (including the laboratories) in water sampling, testing and reporting | Email from Nathan Gedye 15/2/17 indicating the that Inquiry has some concerns about these issues and want them to be addressed by the agencies themselves in the first instance, via the JWG. Response to be drafted/approved/sent | Chair | 2017-03-01 | Generally agreed that JWG agencies should be able to rely on the accreditation/certification/qualification processes used to demonstrate competence of relevant individuals and organisations involved in water sampling testing and reporting. Acknowledged however that recent experiences indicate that such reliance is not always valid. Generally agreed that Ministry of Health review of such processes required.
|  | OTHER ISSUES | ACTION | RESPONSIBILITY | TIMELINE | RISKS / COMMENT / UPDATE | STATUS: Red (off-track); Amber (on-track with issues); Green (on-track)
1 |  | Communications Strategy Whilst communications are generally a corporate issue for each agency represented, agreed that JWG will have a role to play in restoring community trust and confidence | Agreed in general that all agencies releasing communications relating to drinking water will share these with other agencies prior to release, to ensure accuracy and consistency - members to identify the nature and level of such communications Nathan Gedye to publish Action Plan and Minutes on DIA website,which clarifies the transparency around our meetings. Each meeting will be published so recommendation that other stakeholders make provision to publish minutes and Action Plan once a finalised copy is received following each meeting Communications plan to be developed | Members Chair | 2017-04-01 | Draft Comms Plan prepared Members invited to comment Plan to be shared with agency Comms Staff, through CEOs
2 |  | DWA capacity/availability | Confirmation required that HBDHB PHU will provide continuity and sustainability of DWA resource to fulfill local on-site operational requirements, leaving Peter to fulfull secondary/strategic role. | HBDHB |  | DHB will be increasing contracted DWA resource from 1 week to 2 weeks per month from now until June. This is estimated to be an appropriate level of resource to complete the current workload issues. To be reviewed in May. | Completed
3 |  | 12 Month Review | Agreed that JWG will review the potential ongoing utility and scope of such a group beyond the 12 month timeframe - to be placed on the agenda in late 2017 | Chair | 2017-10-01 | Noted for Agenda - Sept 17 May be brought forward in discussions with Mayor/CEOs - refer a) above
NEXT MEETING
Thursday 20 April 2017
3.00pm - 5.00pm
Venue - Napier City Council
- Details TBC
-